|  | Customer |  | Order No. |  |
| --- | --- | --- | --- | --- |
|  | Location |  | Date |  |
|  | PNL No |  | PNL Name |  |

CIRCUIT BREAKER TEST REPORT

- GENERAL DATA AND INFORMATION:

| Serial No |  | Type |  |
| --- | --- | --- | --- |
| Mfg Year |  | Make |  |
| Rated Voltage |  | Rated Current |  |
| Operation Counter |  | Rated Frequency |  |
| Control Voltage |  | Spring Charging Motor Voltage |  |
| Rated Breaking Capacity |  | Rated Making Capacity |  |

#### 2. CHECKLIST:

| ##### Sr.No | ##### DESCRIPTION | ##### Comment |
| --- | --- | --- |
| 2.1 | Visual Inspection for any physical damage or defects. | Yes/No |
| 2.2 | Check nameplate information for correctness. |  |
| 2.3 | Cleaning of circuit breaker with cleaning agent |  |
| 2.4 | Lubrication of operating mechanism & other movable parts |  |
| 2.5 | Checking & rectification of operating mechanism |  |
| 2.6 | Checking of spring charging Manually & Electrically |  |
| 2.7 | Checking of ON-OFF operation Manually & Electrically |  |
| 2.8 | Checking & rectification of breaker contact arm assembly & Tulip contact tightness (Power Connection of breaker) |  |
| 2.9 | Greasing of Tulip Contact with Contact Grease |  |
| 2.10 | Checking the tightness of fasteners, wire connection, spring charging motor, closing, and tripping coil, Limit switches and auxiliary contact |  |
| 2.11 | Checking of mechanical interlocks |  |
|  | - CB can be made ON only in Test & Service position |  |
|  | - CB cannot be made ON in INTERMEDIATE position |  |
|  | - Racking operation can be performed in OFF CB |  |
|  | - Racking operation cannot be performed in ON CB |  |
| 2.12 | Checking & Rectification of racking operation (Breaker test to service condition) or (Breaker service to test Condition) |  |
| 2.13 | Checking & rectification of Limit Switch (Breaker ON -OFF) & Limit Switches (Breaker Test-Service) & Spring Charging Limit Switch. |  |
| 2.14 | Checking of circuit breaker closing & opening Operation in test and Service position |  |
| 2.15 | Checking of Breaker 64 Pin plug socket wire & Pins |  |
| 2.16 | Checking the proper working of VCB trolly |  |
| 2.17 | Checking the setting of shock absorber (Damper setting) |  |

#### 3. BREAKER DATA:

| #### Resistance of Closing Coil |  | #### Resistance of Spring Charging Motor |  |
| --- | --- | --- | --- |
| #### Resistance of Opening Coil |  |

#### 4. CONTACT RESISTANCE TEST (IN MICRO-OHM):

| Injected Test Current CB Close position | Measured contact resistance in micro-ohms |  |  | Acceptable Value |
| --- | --- | --- | --- | --- |
|  | R | Y | B |  |
| Injected Current 100 Amp |  |  |  |  |

5. TIMING TEST (IN MILI SECOND):

| Operation | R | Y | B | Acceptable Value | Control Voltage |
| --- | --- | --- | --- | --- | --- |
| Close |  |  |  |  | 110 VDC |
| Open |  |  |  |  | 110 VDC |

6. INSULATION RESISTANCE VALUE WITH 5 KV MEGGAR

| CB OFF Condition |  |  | Phase to Phase (CB ON Condition) |  |  | Phase to Earth (CB ON Condition) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Before HV | After HV |  | Before HV | After HV |  | Before HV | After HV |
| R – R’ |  |  | R - Y |  |  | R - E |  |  |
| Y - Y’ |  |  | Y - B |  |  | Y - E |  |  |
| B – B’ |  |  | B - R |  |  | B - E |  |  |

7. HV TEST (Applied Voltage for 1 minute =   16 kV)

| Phase | R | Y | B | Acceptable Value |
| --- | --- | --- | --- | --- |
| Leakage current (mA) |  |  |  |  |

8.  COMMENTS & RECOMMENDATIONS:

|  | Test performed by ABB India Ltd | Test witnessed JSW Dolvi |
| --- | --- | --- |
| Name |  |  |
| Signature with Date |  |  |